MINUTES OF MOMENTS

Date: / /

This refers to the visit of M/s Drive and Control System Rajkot to our work Place-Archean Chemicals Industries Limited, Following Points were discussed:

* Installation of SCADA software and other required software Completed
* Panel wiring for data panel were complete and in running status.
* All the ferruling work and labelling work of our panel were completed.
* Development of the SCADA system completed and all the data required by the engineer are implemented in the Scada system.
* All the reporting work for the SCADA generated ass per required format.
* All the programming work for the SCADA system Were completed and under running condition.
* Demonstration of the Scada system were given to the engineers successfully.
* Tap position of the transformer will not show in the Scada because of lake of the module in data panel which will be additional.
* Tap position and temperature of transformer will be added in system online as per we got details from the Supplier.

For Archean Chemical Industries Ltd For Drive and Control System